## FlowLogic Receiver
SUL-13-218
Sullair FlowLogic
Air Receiver Sizing Calculator
Inputs
Total Compressor Capacity (CFM) |  |  | 2732 |  | CFLP |  | FCSP | MDP
[5 empty] | 125 | 115 | 110 | 5
Compressor Full Load Pressure (psig) |  |  | 125
CRSDP
CRS Pressure Drop - DP (psid) |  |  | 10 |  | 10 |  | Result | Display
[7 empty] | 15018.8482 | 15018.8482
Flow Controller Set Point (psig) |  |  | 110 |  | TCC
[5 empty] | 2732 | 1366
Maintianed Differential Pressure (psi) |  |  | 5
Result
Recommended Receiver Size (Gallons) |  |  | 15018.8482
Sullair FlowLogic
Useable Air Stored Calculator
RS
|  |  | Inputs |  | 6872 | 6872 | 918.6552
Receiver Size (Gallons) |  |  | 6872 |  |  |  |  | Result
[6 empty] | CFLP |  | 633.5553
Compressor Full Load Pressure (psig) |  |  | 110 |  |  | 110
Total Sys
CRS Pressure Drop - DP (psid) |  |  | 10 |  |  | CRSDP |  | 2534.2212
10
Flow Controller Set Point (psig) |  |  | 90
FCSP
Maintianed Differential Pressure (psi) |  |  | 10 |  |  | 90
|  |  | Results |  |  | MDP
Useable Air Stored (SCF) |  |  | 633.5553 |  |  | 10
Total System Capacity this can support: |  |  | 2534.2212 | CFM
NOTES
1. | The above calculators are "Rules of Thumb" only. No performance guarantees are stated or implied.
2. | The best way to optimize storage for a specific application is to conduct a detailed system assessment.
3. | Calculations are based upon having stored energy to support 50% above the total compressor capacity for 30 seconds.
4. | Useable Air Stored is in cubic feet of air that can be drawn from storage to support a 30 second event at a given differential pressure. (storage pressure-set pressure)
This file contains information that is confidential and proprietary to Sullair. As a condition of and as consideration for receiving this file, the recipient agrees that this file and the information contained therein shall not be disclosed to others or duplicated without the written permission of Sullair.
For more information, |  | www.sullair.com | Sullair Proprietary and Confidential
contact Sullair at 219.879.5451 or |  |  | © 2013 Sullair, LLC
sullairsolutions@sullair.com