## FlowLogic Savings
[5 empty] | CHP |  |  | LOAD/ NOLOAD |  | INLET MOD W NO BLOWDOWN |  | INLER MOD W BLOWDOWN |  | VARIABLE DISPLACEMENT |  | VARIABLE SPEED |  | VARIABLE SPEED W/ SPIRAL VALVE
|  |  | SUL-13-217 |  | 100
Sullair FlowLogic | [6 empty] | Motor effic. |  | 95.8%
Annual Energy Savings Estimator |  |  |  |  | FLP
Compressor Control Type: |  |  | Load/Unload |  | 125 |  | Full Load KW: |  | 77.8706
Compressor Rated bHP |  |  | 100 |  | FLC |  | Percent Capacity: |  | 0.5 |  |  | Perct power sub cals no flowlogic |  | Perct power sub cals w/o flowlogic |  | Perct power sub cals w/o flowlogic |  | Perct power sub cals w/o flowlogic
[5 empty] | 450 |  | Percent Capacity w/FlowLogic: |  | 0.4552 |  |  | 0 to 40 | 0.9625 | 0 to 40 | 0.6875 | 0 to 20 | 0.625 | 0 to 20 | 0.605
Main Motor Efficiency: (i.e. 95.0%) |  |  | 95.8% |  |  |  | Time Loaded seconds: |  | 73.7655 |  |  | 41 to 100 | 0.85 | 41 to 50 | 0.62 | 21 to 100 | 0.53125 | 21 to 39 | 0.524
[5 empty] | SS | [8 empty] | 51 to 100 | 0.62 |  |  | 40 to 50 | 0.53
Rated Full Load Capacity: (CFM) |  |  | 450 |  | 3000 |  | Time Unloaded seconds: |  | 43.7655 | [6 empty] | Perct power sub cals w/Flowlogic |  | 51 to 59 | 0.53
[12 empty] | Perct power sub cals w flowlogic |  |  |  | 0 to 20 | 0.569 | 60 to 100 | 0.5
Avg. Compressor Discharge Pressure: (PSIG) |  |  | 125 |  | CVD | Demand w/FlowLogic | Time Cycling seconds: |  | 30 |  |  | 0 to 40 | 0.89866 | Perct power sub cals |  | 21 to 100 | 0.48925
[5 empty] | 225 | 204.8387 | [5 empty] | 41 to 100 | 0.83656 | 0 to 40 | 0.6483 |  |  | Perct power sub cals w/flowlogic
CRS Pressure Drop DP (PSID) |  |  | 0 |  |  |  | Total Time: |  | 147.531 |  |  |  |  | 41 to 50 | 0.61104 |  |  | 0 to 20 | 0.55079
[5 empty] | EC | [8 empty] | 51 to 100 | 0.58595 |  |  | 21 to 39 | 0.48189
Average Delivered/System Pressure (PSIG) |  |  | 125 |  | 0.1 |  | Perct Time Loaded: |  | 50% | [8 empty] | 40 to 50 | 0.4852
[18 empty] | 51 to 59 | 0.49864
System Strorage Volume: (Gallons) |  |  | 3000 |  | FCSP |  | Perct Time Unloaded: |  | 29.67% | [8 empty] | 60 to 100 | 0.4552
100
Current Average Demand: (CFM) |  |  | 225 |  |  |  | Percet Time Cycling: |  | 20.33%
Cont type
Percent of Current Demand Effectively Regulated |  |  | 50% |  | Load/Unload |  | Perct Power: |  | 71.38% | Perct. Power w/o Flowlogic | 0.85 | Perct power w/o flowlogic | 0.85 | Perct. Power w/o flowlogic | 0.62 | Perct Powerw/o flowlogic: | 0.53125 | Perct Power w/o flowlogic: | 0.53
[5 empty] | Inlet Mod no blow down |  |  |  |  | Perct. Power w/ Flowlogic | 0.83656 | Perct power w/ flowlogic | 0.83656 | Perct. Power w flowlogic | 0.61104 | Perct Power w flowlogic: | 0.48925 | Perct Power w/flowlogic: | 0.4852
FlowLogic Controller Set Point: (PSIG) |  |  | 100 |  | Inlet mod with blow down |  | Current KW: |  | 55.5805 | Current KW: | 66.19 | Current KW: | 66.19 | Current KW: | 48.2797 | Current KW: | 41.3687 | Current KW: | 41.2714
[5 empty] | variable displacment |  |  |  |  | KW with FlowLogic | 65.1433 | KW w/Flowlogic | 65.1433 | KW with Flowlogic | 47.582 | KW with Flowlogic | 38.098 | KW with Flowlogic | 37.7826
Energy Costs: ($/KWH) |  |  | 0.1 |  | Variable Speed |  | Annual Operating cost at current kw w/o flowlogic: |  |  | Annual Operating cost at current kw w/o flowlogic: |  | Annual Operating cost at current kw w/o flowlogic: |  | Annual Operating cost at current kw w/o flowlogic: |  | Annual Operating cost at current kw w/o flowlogic: |  | Annual Operating cost at current kw w/o flowlogic:
[5 empty] | variable speed with spiral valve |  |  |  | 48688.5314 |  | 57982.4217 |  | 57982.4217 |  | 42293.0605 |  | 36239.0136 |  | 36153.7453
Annual Hours of Operation |  |  | 8760
[5 empty] | Display outputs |  | Operating cost per sec: |  |  | Operating cost per sec: |  | Operating cost per sec: |  | Operating cost per sec: |  | Operating cost per sec: |  | Operating cost per sec:
Operating Costs Without FlowLogic Controller | [8 empty] | 0.0015439 |  | 0.0018386 |  | 0.0018386 |  | 0.0013411 |  | 0.0011491 |  | 0.0011464
Load/Unload
Operating Costs: |  |  | 48688.5314 |  |  |  | Power savings with flowlogic: |  |  | Power savings with flowlogic: |  | Power savings with flowlogic: |  | Power savings with flowlogic: |  | Power savings with flowlogic: |  | Power savings with flowlogic:
[5 empty] | W/O flowlogic costs | 48688.5314 |  |  | 2.7515 |  | 1.0466 |  | 1.0466 |  | 0.69776 |  | 3.2708 |  | 3.4888
Operating Costs With FlowLogic Controller
[5 empty] | W flow logic costs | 46278.2028 | Annual Operating cost with flowlogic: |  |  | Annual Operating cost with flowlogic: |  | Annual Operating cost with flowlogic: |  | Annual Operating cost with flowlogic: |  | Annual Operating cost with flowlogic: |  | Annual Operating cost with flowlogic:
Operating Costs: |  |  | 46278.2028 | [5 empty] | 46278.2028 |  | 57065.5586 |  | 57065.5586 |  | 41681.8185 |  | 33373.8164 |  | 33097.535
[5 empty] | Savings | 2410.3285
New Average Demand |  |  | 204.8387 | cfm |  |  | Operating costs per sec with flowlogic: |  |  | Operating costs per sec with flowlogic: |  | Operating costs per sec with flowlogic: |  | Operating costs per sec with flowlogic: |  | Operating costs per sec with flowlogic: |  | Operating costs per sec with flowlogic:
[5 empty] | HRS |  |  |  | 0.0014675 |  | 0.0018095 |  | 0.0018095 |  | 0.0013217 |  | 0.0010583 |  | 0.0010495
Annual Savings: |  |  | 2410.3285 |  | 8760
[7 empty] | Annual Savings: |  | 2410.3285 | Annual Savings: | 916.8631 | Annual Savings: | 916.8631 | Annual Savings: | 611.2421 | Annual Savings: | 2865.1972 | Annual Savings: | 3056.2103
Assumes: | 14.5 psia atmospheric pressure, 25% unloaded power, 10 psig control band and 30 seconds unload time | [5 empty] | With FlowLogic
[7 empty] | Percent Capacity w/FlowLogic: |  | 0.4552
This file contains information that is confidential and proprietary to Sullair. As a condition of and as consideration for receiving this file, the recipient agrees that this file and the information contained therein shall not be disclosed to others or duplicated without the written permission of Sullair.
[7 empty] | Time Loaded: |  | 67.6993
For more information, contact Sullair at 219.879.5451 or |  | www.sullair.com | Sullair Proprietary and Confidential |  |  |  | Time Unloaded: |  | 51.0259
sullairsolutions@sullair.com |  |  | © 2013 Sullair, LLC
[7 empty] | Time Cycling: |  | 30
[7 empty] | Total Time: |  | 148.7252
[7 empty] | Perct Time Loaded: |  | 45.52%
[7 empty] | Perct Time Unloaded: |  | 34.31%
[7 empty] | Percet Time Cycling: |  | 20.17%
[7 empty] | Perct Power: |  | 67.84%
[7 empty] | Current KW: |  | 52.829